## Design Calculations
DESIGN BASIS

Design Data:

	Concrete grade	M 20
	Steel Grade	Fe 415
	Density of RCC	25	kN/m^3
	Density of water	10	kN/m^3
	Density of soil (dry)	18.5	kN/m^3
	Density of soil (saturated)	20	kN/m^3
	: Angle of internal friction	29.5	o
	: Coeff. of active earth pressure	0.34

Min. Clear Cover

	Faces in contact with water	25	mm
	Faces in contact with soil	40	mm
	Free faces	25	mm

REFERENCES – Codes and Standards

	IS 456 – 2000 Plain and Reinforced Concrete - Code of Practice
	IS 875 – 1987 Code of practice for design loads for buildings and structures
	IS 3370 – 1967 Concrete structures for the storage of liquids - Code of practice

## Data
fck	20
fy	415
denConc	25
denWater	10
denSoilDry	18.5
denSoilSatu	20
AngleIntFric	29.5
ccWater	25	ClearCover
ccSoil	40
ccFree	25
freeBoard	200

## Sheet3
	3.14159265358979

	D	H	Vol	Lakh litre	30H+50		H^2/DT
	12.5	1.83	224574.787346458	2.24574787346458	104.9	150	1.8
	6	1.77	50045.5709716854	0.500455709716854	103.1	150	3.5
	11.2	3.05	300487.054130556	3.00487054130556	141.5	150	5.5
		H	1.83	D	11.8	Thickness	200
	Total Ht	2.03
Fix Base		Water	Soil	Hinge Base	Water	Soil
T	0.27	32.3379	21.989772	0.41	49.1057	33.391876
M	0.05	4.1827135	2.84424518	0.024	2.00770248	1.3652376864

			450	0.2
			100	0.3
	Min Steel	0.271428571428571					8	50.2654824574367
	HYSD	0.217142857142857					10	78.5398163397448
	Ast	434.285714285714	mm2				12	113.097335529233
	Ast per layer	217.142857142857					16	201.061929829747
	Spacing
	8	231.485774475037
	10	361.696522617246

## DomeCir
Dia/Rise		[ 5 to 8]
1.475	to	2.36
RiseClear	3.55	mm				LL	1.5
Thickness	100	mm				SelfWt	2.5
RiseCenter	3.6	m	RiseOpening			Other dead load	0
DiaCenter	12	m	DiaOpening	2	m	Total DL	2.5
Dia/rise	3.33333333333333					TDL+LL	4	kN/m^2
radiusDomeCen	6.8
radiusDomeClear	6.75	m

sinTheta	0.882352941176471		sinAlpha	0.147058823529412
Theta	61.927513064147	degrees	Alpha	8.45651933527051	degrees
	1.08083900054117	radians		0.147594105659033	radians
cosTheta	0.470588235294118		cosAlpha	0.989127748282367